## Blad1
Lansen MIOTY protocol description
"name":"LAN-MIOTY-E2-CO2-S-I",
article:"LAN-920-0054",
Index | Name | Context | Val | Uplink | Interger | Numeric | Min | Max | Resolution | Calculations
[5 empty] | unsigned | Unit |  |  |  | Max/Min calc | Needed values | Needed bits | Full bits
0 | temp_1 | Current measured temperature |  | 1 |  | °C | -10 | 50 | 0.125 | 61 | 488 | 8.9307 | 9
1 | humidity_1 | Current measured humidity |  | 1 |  | %RH | 0 | 100 | 1 | 101 | 101 | 6.6582 | 7
2 | co2_1 | Current measured CO2 |  | 1 |  | ppm | 0 | 5000 | 20 | 5001 | 250.05 | 7.9661 | 8
3 | sound_1 | Current measured sound level |  | 1 |  | dBA | 40 | 100 | 1 | 61 | 61 | 5.9307 | 6
4 | temp_2 | Previous measured temperature |  | 1 |  | °C | -10 | 50 | 0.125 | 61 | 488 | 8.9307 | 9
5 | humidity_2 | Previous measured humidity |  | 1 |  | %RH | 0 | 100 | 1 | 101 | 101 | 6.6582 | 7
6 | co2_2 | Previous measured CO2 |  | 1 |  | ppm | 0 | 5000 | 20 | 5001 | 250.05 | 7.9661 | 8
7 | sound_2 | Previous measured sound level |  | 1 |  | dBA | 40 | 100 | 1 | 61 | 61 | 5.9307 | 6
8 | batt | Current battery voltage |  | 1 |  | V | 1.9 | 3.3 | 0.1 | 2.4 | 24 | 4.585 | 5
9 | co2_last_calibration_value | Last calibrated CO2-value |  | 1 |  | ppm | 0 | 5000 | 20 | 5001 | 250.05 | 7.9661 | 8
10 | days_to_next_calibration | Number of days until next CO2 calibration |  | 1 |  | days | 0 | 31 | 1 | 32 | 32 | 5 | 5
11 | calibration_not_done | Calibration not done yet, give it some more hours |  | 1 | 1 | %01 |  |  | 1 | 1 | 1 | 0 | 1
12 | co2_error | Error detected on the CO2-module |  | 1 | 1 | %01 |  |  | 1 | 1 | 1 | 0 | 1
13 | unused | unused
80